OCTOBER 2021

|  |  |  |
| --- | --- | --- |
|  |  |  |

**Product Guide Specification**

Specifier Notes: This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, based on *MasterFormat 2016* and *The Project Resource Manual—CSI Manual of Practice. The Manufacturer is responsible for technical accuracy.*

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code. Words and sentences within brackets [ ] are choices to include or exclude a particular item or statement. Coordinate this section with other specification sections and the Drawings. Delete all “Specifier Notes” after editing this section.

**Section 28 21 00: Video Surveillance**

**Section 28 21 13: IP Cameras**

**12 MP 360° IR NETWORK FISHEYE CAMERA**

1. **– GENERAL**
	1. SUMMARY
		1. Section Includes
			1. Section 28 21 17: Video Surveillance – Surveillance Cameras – Camera Housings
			2. Section 28 21 19: Video Surveillance – Surveillance Cameras – Camera Mounts
			3. Section 28 21 21: Video Surveillance – Surveillance Cameras – Illuminators
			4. Section 28 27 00: Video Surveillance – Video Surveillance Sensors
		2. Related Sections
			1. [Section 28 33 15: Security Detection, Alarm and Monitoring – Security Monitoring and Control – Security Monitoring and Control Software].

\*\*\*\*\*\*\*\*\*\*Specifier’s note: Include those standards referenced elsewhere in this SECTION.

* 1. REFERENCES
		1. Federal Communications Commission (FCC) ([www.fcc.gov](http://www.fcc.gov))
			1. FCC Part 15 Subpart B
		2. HD standards
			1. Complies with the SMPTE 274M-2008 Standard in:
				1. Resolution: 1920x1080
				2. Scan: Progressive
				3. Color representation: complies with ITU-R BT.709
				4. Aspect ratio: 16:9
				5. Frame rate: 25 and 30 frames/s
			2. Complies with the 296M-2001 Standard in:
				1. Resolution: 1280x720
				2. Scan: Progressive
				3. Color representation: complies with ITU-R BT.709
				4. Aspect ratio: 16:9
				5. Frame rate: 25, 30, 50 and 60 frames/s
				6. Interference-Causing Equipment Standards
	2. SYSTEM DESCRIPTION
		1. Section Includes
			1. Video Surveillance – Surveillance Cameras – IP Cameras
		2. Performance Requirements
			1. The 12 MP Fisheye camera shall be a full-featured 360° fisheye-lens camera designed for discrete video surveillance applications in indoor environments.
			2. The 12 MP Fisheye camera shall provide direct network connection using Smart H.265+ and Smart H.264+ compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.
			3. The 12 MP Fisheye camera shall offer an automatic day/night filter that delivers color images during daylight and electronically switches to a monochrome image as the scene darkens.
			4. The 12 MP Fisheye camera shall offer multiple dewarping modes for different installations and configurations, either with a Dahua XVR or an NVR.
			5. The 12 MP Fisheye camera shall be a high performance 1/1.7-in. progressive-scan STARVIS™ CMOS sensor with 12 MP resolution.
			6. The 12 MP Fisheye camera shall support the following dual, redundant power options:
				1. 12 VDC
				2. PoE+ (IEEE 802.3at, class 4)
				3. The 12 MP Fisheye camera shall default to use power from the PoE power supply, if connected.
				4. The 12 MP Fisheye camera shall reboot and switch to the 12 VDC power supply if power from the PoE power supply is lost.
			7. The 12 MP Fisheye camera shall come with a built-in microphone and a built-in speaker.
			8. The 12 MP Fisheye camera shall offer Digital Wide Dynamic Range for clear images in extreme high-contrast environments.
			9. The 12 MP Fisheye camera shall offer Analytics+ features for people counting and queue management.
			10. The 12 MP Fisheye camera shall conform to the ONVIF standard to provide interoperability with other conformant systems.
			11. The 12 MP Fisheye camera shall offer three separate and configurable streams with individually configurable streams.
			12. The 12 MP Fisheye camera shall have a fixed lens with a focal length of
			1.85 mm.
			13. The 12 MP Fisheye camera shall be certified to the IP67 Ingress Protection rating.
			14. The 12 MP Fisheye camera shall be certified to the IK10 Vandal Resistance rating.

SUBMITTALS

* + 1. Submit under provisions of Section [01 33 00.]
		2. Product Data:
			1. Manufacturer’s data, user and installation manuals for all equipment and software programs including computer equipment and other equipment required for complete video management system.
		3. Dimensional Drawings; include
			1. Overall device dimensions.
			2. Dimensions specific for installation.
		4. Closeout Submittals
			1. User manual.
			2. Parts list.
			3. Maintenance requirements.
	1. QUALITY ASSURANCE
		1. Manufacturer:
			1. Minimum of [10] years of experience in manufacture and design Video Surveillance Devices.
		2. Video Surveillance System:
			1. List certifying bodies (UL, CSA, etc.)
			2. Provide evidence of compliance upon request.
		3. Installer:
			1. Minimum of [5] years of experience installing Video Surveillance System.
	2. DELIVERY, STORAGE AND HANDLING
		1. Comply with requirements of Section 01 60 00.
		2. Deliver materials in manufacture’s original, unopened, undamaged containers; and unharmed original identification labels.
		3. Protect store materials from environmental and temperature conditions following manufacturer’s instructions.
		4. Handle and operate products and systems according to manufacturer’s instructions.
	3. WARRANTY
		1. Provide manufacturer’s warranty covering [2] years for replacement and repair of defective equipment. Warranty varies country to country.
	4. MAINTENANCE
		1. Make ordering of new equipment for expansions, replacements, and spare parts available to dealers and end users.
		2. Provide factory direct technical support via phone and e-mail.
1. **– PRODUCTS**
	1. MANUFACTURERS
		1. [Acceptable Manufacturer:

15245 Alton Parkway, Suite #100

Irvine, CA 92618

Tel: (949) 679-7777

Fax: (949) 679-5760

Email: sales.usa@dahuatech.com]

* + 1. Substitutions: [Not permitted.] [Under provisions of Division 1.]
			1. [All proposed substitutions must be approved by the Architect or Engineer professional.]
			2. [Proposed substitutions must provide a line-by-line compliance documentation.]
	1. 12 MPIR NETWORK FISHEYE CAMERA DH-IPC-EBW81242N-AS-S2

		1. General Characteristics:
			1. The 12 MP Fisheye camera shall be a full-featured 360° fisheye-lens camera designed for discrete video surveillance applications in indoor environments.
			2. The 12 MP Fisheye camera shall provide direct network connection using Smart H.265+ and Smart H.264+ compression and bandwidth throttling to efficiently manage bandwidth and storage requirements while delivering outstanding image quality.
			3. The 12 MP Fisheye camera shall offer an automatic day/night filter that delivers color images during daylight and electronically switches to a monochrome image as the scene darkens.
			4. The 12 MP Fisheye camera shall offer multiple dewarping modes for different installations and configurations, either with a Dahua XVR or an NVR.
			5. The 12 MP Fisheye camera shall be a high performance 1/1.7-in. progressive-scan STARVIS™ CMOS sensor with 12 MP resolution.
			6. The 12 MP Fisheye camera shall support the following dual, redundant power options:
				1. 12 VDC
				2. PoE+ (IEEE 802.3at, class 4)
				3. The 12 MP Fisheye camera shall default to use power from the PoE power supply, if connected.
				4. The 12 MP Fisheye camera shall reboot and switch to the 12 VDC power supply if power from the PoE power supply is lost.
			7. The 12 MP Fisheye camera shall come with a built-in microphone and a built-in speaker.
			8. The 12 MP Fisheye camera shall offer Digital Wide Dynamic Range for clear images in extreme high-contrast environments.
			9. The 12 MP Fisheye camera shall offer Analytics+ features for people counting and queue management.
			10. The 12 MP Fisheye camera shall conform to the ONVIF standard to provide interoperability with other conformant systems.
			11. The 12 MP Fisheye camera shall offer three separate and configurable streams with individually configurable streams.
			12. The 12 MP Fisheye camera shall have a fixed lens with a focal length of
			1.85 mm.
			13. The 12 MP Fisheye camera shall be certified to the IP67 Ingress Protection rating.
			14. The 12 MP Fisheye camera shall be certified to the IK10 Vandal Resistance rating.
		2. Imaging
			1. The 12 MP Fisheye camera shall offer a 1/1.7-inch progressive-scan CMOS imager.
			2. The 12 MP Fisheye camera shall offer 4000 x 3000 effective picture elements.
			3. The 12 MP Fisheye camera shall offer a fixed lens with a focal length of
			1.85 mm.
			4. The 12 MP Fisheye camera shall produce a 185° horizontal angle of view and a 180° vertical angle of view.
			5. The 12 MP Fisheye camera shall offer a maximum aperture of F2.0.
			6. The 12 MP Fisheye camera shall produce a color image with a minimum scene illumination of 0.01 lux at F2.0 (1/3 s, 30 IRE) and 0 lux at F2.0 with IR illumination.
		3. Video Characteristics
			1. The 12 MP Fisheye camera shall offer CBR/VBR bit rate control.
			2. The 12 MP Fisheye camera shall offer the following video compression protocols
				1. H.265 (3 Kbps to 16384 Kbps)
				2. H.264 (8 Kbps to 16384 Kbps)
			3. The 12 MP Fisheye camera shall offer BLC, HLC, and Digital WDR modes of backlight compensation.
			4. The 12 MP Fisheye camera shall offer Auto, Natural, Street Lamp, Outdoor, Manual, and Regional Custom white balance mode.
			5. The 12 MP Fisheye camera shall offer 3D DNR noise reduction.
			6. The 12 MP Fisheye camera shall offer motion detection (four zones) and region of interest (four zones) controls.
			7. The 12 MP Fisheye camera shall offer four (4) privacy masking areas.
		4. Streaming Capability
			1. The 12 MP Fisheye camera shall generate full 12 MP
			(4000 x 3000 pixels) at 30 fps resolution using H.265 compression.
			2. The 12 MP Fisheye camera shall offer Unicast and Multicast streaming methods.
			3. The 12 MP Fisheye camera shall offer the following resolutions:
				1. 12 MP (4000 x 3000)
				2. 8 MP (2880 x 2880)
				3. 2880 x 2160
				4. 3 MP (2048 x 1536)
				5. 1.3 MP (1280 x 960)
				6. D1 (704 x 480)
				7. CIF (352 x 240)
			4. The 12 MP Fisheye camera shall generate three (3) streams at the following maximum resolutions:
				1. Main Stream: 12 MP at 25 fps
				2. Sub Stream 1: D1 at 30 fps
				3. Sub Stream 2: 1280 x 96017 fps
		5. IP Connectivity
			1. The 12 MP Fisheye camera shall allow full camera control and configuration capabilities via a TCP/IP network.
			2. The 12 MP Fisheye camera shall deliver 12 MP video, at rates up to 25 frames per second via TCP/IP over an RJ-45 (10/100 Base-T) connection.
			3. The 12 MP Fisheye camera shall conform to the ONVIF and the CGI standard.
			4. The 12 MP Fisheye camera shall offer Quality of Service (QoS) configuration options.
			5. The 12 MP Fisheye camera shall support the IPv6 internet-layer protocol for packet switched internetworking across multiple IP networks.
			6. The 12 MP Fisheye camera shall offer local and network storage options that include: MicroSD and FTP.
			7. The 12 MP Fisheye camera shall support the following protocols: IPv4/ IPv6, HTTP, SSL, TCP/IP, UDP, UPnP, ICMP, IGMP, SNMP, RTSP, RTP, SMTP, NTP, DHCP, DNS, PPPOE, DDNS, FTP.
			8. The 12 MP Fisheye camera shall support the Smart PSS and DSS management software.
			9. The 12 MP Fisheye camera shall support the Android and the IOS mobile operating systems.
		6. Interface
			1. The 12 MP Fisheye camera shall offer one (1) built-in microphone and one (1) built-in speaker. .
			2. The 12 MP Fisheye camera shall offer two (2) alarm input channels
			(Wet Contact, 3 V to 5 V) and two (2) alarm relays (Dry Contact, 30 V).
		7. Advanced Analytics
			1. The Intelligent Video System shall offer the following advanced analytics built-in to the 12 MP Fisheye camera:
				1. Perimeter protection detects human or vehicle violations using tripwire or intrusion detection.
				2. People counting delivers accurate flow statistics from four (4) distinct, user-defined region.
				3. Queue management monitors four (4) user-defined regions where people wait in line (or queue)
		8. Intelligent Video System
			1. The 12 MP Fisheye camera offer a built-in Intelligent Video System to provide advanced analytics for any scene.
			2. The Intelligent Video System shall offer intelligent video analytics built-in to the 12 MP Fisheye camera.
			3. The Intelligent Video System shall be capable of processing and analyzing video within the camera itself, with no extra hardware required.
			4. The Intelligent Video System shall trigger an alarm and take a defined action for the following events:
				1. Standard Features

Tampering with the camera.

Error writing to an onboard Micro SD Card.

Error sending or receiving data over the network.

Unauthorized access to the camera.

* + - * 1. Premium Features

Tripwire: a target crosses a user-defined line.

Intrusion: a target enters or exits a defined perimeter.

* + - * 1. Advanced Features

Heat Map: generates a visual representation of data.

* + 1. Installation Requirements
			1. The 12 MP Fisheye camera shall be capable of operating in an indoor environment within a temperature range of -40 °C to +60 °C (-40 °F to +140 °F).
			2. The 12 MP Fisheye camera shall accept power, transmit video, and accept control via a TCP/IP connection.
			3. The 12 MP Fisheye camera shall support the following dual, redundant power options:
				1. 12 VDC
				2. PoE+ (IEEE 802.3at, class 4)
				3. The 12 MP Fisheye camera shall default to use power from the PoE power supply, if connected.
				4. The 12 MP Fisheye camera shall reboot and switch to the 12 VDC power supply if power from the PoE power supply is lost.
		2. Housing Options
			1. The 12 MP Fisheye camera shall be offered in a metal housing.
			2. The 12 MP Fisheye camera shall be certified to the IP67 Ingress Protection rating.
			3. The 12 MP Fisheye camera shall be certified to the IK10 Vandal Resistance rating.
	1. ACCESSORIES
		1. The 12 MP Fisheye camera shall offer the following optional accessories:
			1. [Mount adapter.]
			2. [Junction box.]
			3. [Ceiling Mount.]
			4. [Wall mount.]
			5. [Pole mount.]
			6. [Fisheye-PTZ integrated wall mount.]
			7. [Power adapter.]
1. **– EXECUTION**
	1. EXAMINATION
		1. Examine areas to receive devices and notify adverse conditions affecting installation or subsequent operation.
		2. Do not begin installation until unacceptable conditions are corrected.
	2. PREPARATION
		1. Protect devices from damage during construction.
	3. INSTALLATION
		1. Install devices in accordance with manufacturer’s instruction at locations indicated on the floor drawings plans.
		2. Perform installation with qualified service personnel.
		3. Install devices in accordance with the National Electrical Code or applicable local codes.
		4. Ensure selected location is secure and offers protection from accidental damage.
		5. Location must provide reasonable temperature and humidity conditions, free from sources of electrical and electromagnetic interference.
	4. FIELD QUALITY CONTROL
		1. Test snugness of mounting screws of all installed equipment.
		2. Test proper operation of all video system devices.
		3. Determine and report all problems to the manufacturer’s customer service department.
	5. ADJUSTING
		1. Make proper adjustment to video system devices for correct operation in accordance with manufacturer’s instructions.
		2. Make any adjustment of camera settings to comply with specific customer’s need.
	6. DEMOSTRATION
		1. Demonstrate at final inspection that video management system and devices functions properly.

END OF SECTION